## Cover
Clean Air Buildings
By Walter Sobkiw
2023-01-30
4/22/2020 origination
This research is not associated with any institution.
It is ongoing and part of a broader set of COVID-19 systems oriented research areas.
www.cassbeth.com/covid-19
This spreadsheet houses many of the tables used in the return to life systems analysis.
Select the appropriate tabs.
Copyright 2022. This spreadsheet may be freely distributed and referenced as long as the author is clearly identified. When using this paper for critical review or significant meetings the author requests that he be contacted and made aware of the events. Any publication works that will collect money from part or all of this content must contact the author.

## ACH Calc Ex
ACH calculations for a Generic space one vent type
Site Survey Element | Data | Comments
Facility Name | Restaurant
Room Name | NA
Room Size
length ft | 64 | 16 windows X 4 ft
width ft | 30 | 10 windows X 3 ft
sq feet | 1920
height ft | 20 | estimated
cubic feet | 38400
Vents
vent length inches | 48
vent width inches | 48
number of vents | 2
vent sq inches | 4608
vent sq feet | 32
CFM
measured air ft per min | 200
cubic feet per min CFM | 6400
cubic feet per hour CFH | 384000
total CFH | 384000
Results
ACH (total CFH/cubic feet) | 10
ACH calculations for a Generic space different vent types
Site Survey Element | Data | Comments
Facility Name | Restaurant
Room Name | NA
Room Size
length ft | 64 | 16 windows
width ft | 30 | 10 windows
sq feet | 1920
height ft | 20 | estimated
cubic feet | 38400
Vents | vent type A | vent type B
vent length inches | 3 | 12
vent width inches | 36 | 36
number of vents | 6 | 9
vent sq inches | 648 | 3888
vent sq feet | 4.5 | 27
CFM
measured air ft per min | 200 | 200
cubic feet per min CFM | 900 | 5400
cubic feet per hour CFH | 54000 | 324000
total CFH |  |  | 378000
Results
ACH (total CFH/cubic feet) | 9.8438
ACH calculations for a Generic space where the following data is provided
Site Survey Element | Data | Comments
Facility Name | Airport
Room Name | NA
Room Size
building(s) square feet | 7000000 | Total facility with all buildings
Assumed average ceiling height | 20
building(s) cubic feet | 140000000
CFM
Cubic feet per min (CFM) | 11000000 | AHUs push nearly 11 million cubic feet of air each minute
Cubic feet per hour (CFH) | 660000000
Results
ACH (CFH/buildings cubic feet) | 4.7143 | 4.7143

## eACH Calc
FAR UV
https://rzero.com/vive/?utm_source=JSJD-Google&utm_medium=cpc&utm_campaign=rZero-Search&utm_content=Vive&CID=JSJDGoogleCPC
| ceiling | 9
meters | feet | % room height | time sec | time min | eACH | eACH slice
0.5 | 1.64 | 0.18222 | 30 | 0.5 | 120 | 21.8667
1.5 | 4.92 | 0.54667 |  | 4.5 | 13.3333 | 7.2889
2.5 | 8.2 | 0.91111 |  | 12.4 | 4.8387 | 4.4086 | 14.5778 | eACH avg 3 foot from floor level
[6 empty] | 11.1881 |  | eACH avg floor level
|  |  | eACH avg 3 foot from floor level | 14.5778
|  |  | eACH avg floor level | 11.1881

## Facility
Copy and paste appropriate tab data for each room in the facility
Site Survey Element | Data | Comments
Facility Name | Clubhouse
Room Name | Ball Room
Room Size
length ft | 64
width ft | 30
sq feet | 1920
height ft | 20
cubic feet | 38400
Vents
vent length inches | 48
vent width inches | 48
number of vents | 2
vent sq inches | 4608
vent sq feet | 32
CFM
measured air ft per min | 200
cubic feet per min CFM | 6400
cubic feet per hour CFH | 384000
total CFH | 384000
Results
ACH (total CFH/cubic feet) | 10

## Vents
4-Way Diffuser Sizes
Airflow (cfm) | Diffuser Size | Neck Size (in) | Linear FPM | area in | area ft | A=πr^2 | https://aircondlounge.com/hvac-diffuser-sizing-guide-cfm-chart-selection/
150 | 2 ft x 2 ft | 8 | 429.5455 | 50.2857 | 0.34921 |  | HVAC diffusers should be based on an airflow of around 250 CFM and a noise level of below NC30. 2 ft length by 2 ft width and 8 inches inlet diameter is the most common size for a 4-way ceiling diffuser.
200 | 2 ft x 2 ft | 8 | 572.7273 | 50.2857 | 0.34921
250 | 2 ft x 2 ft | 10 | 458.1818 | 78.5714 | 0.54563
300 | 2 ft x 2 ft | 10 | 549.8182 | 78.5714 | 0.54563
350 | 2 ft x 2 ft | 12 | 445.4545 | 113.1429 | 0.78571
400 | 2 ft x 2 ft | 12 | 509.0909 | 113.1429 | 0.78571
450 | 2 ft x 2 ft | 14 | 420.7792 | 154 | 1.0694
500 | 2 ft x 2 ft | 14 | 467.5325 | 154 | 1.0694
Linear Diffuser Sizes
Airflow (cfm) | Diffuser Size | Neck Size (in)
50 | 1-slot, 2 ft | 6 | 254.5455 | 28.2857 | 0.19643 |  | 50mm/slot or 1.95 inches/slot
100 | 2-slot, 2 ft | 8 | 286.3636 | 50.2857 | 0.34921
150 | 2-slot, 4 ft | 8 | 429.5455 | 50.2857 | 0.34921
200 | 2-slot, 4 ft | 10 | 366.5455 | 78.5714 | 0.54563
250 | 3-slot, 4 ft | 8 | 715.9091 | 50.2857 | 0.34921
300 | 3-slot, 4 ft | 10 | 549.8182 | 78.5714 | 0.54563
350 | 4-slot, 4 ft | 10 | 641.4545 | 78.5714 | 0.54563
400 | 4-slot, 4 ft | 12 | 509.0909 | 113.1429 | 0.78571
Horizontal Return Air Grilles
Grille Area (sq.in) | Grille Size (in) | Airflow (cfm) | FPM |  |  |  | https://aircondlounge.com/return-air-grille-sizing-guide-cfm-chart-calculation
24 | 4 x 6 | 58 | 348
48 | 4 x 12 | 117 | 351
60 | 6 x 10 | 146 | 350.4
180 | 6 x 30 | 438 | 350.4
128 | 8 x 16 | 311 | 349.875
144 | 8 x 18 | 350 | 350
192 | 8 x 24 | 467 | 350.25
240 | 8 x 30 | 583 | 349.8
256 | 8 x 32 | 622 | 349.875
200 | 10 x 20 | 486 | 349.92
220 | 10 x 22 | 535 | 350.1818
240 | 10 x 24 | 583 | 349.8
300 | 10 x 30 | 729 | 349.92
216 | 12 x 18 | 525 | 350
240 | 12 x 20 | 583 | 349.8
288 | 12 x 24 | 700 | 350
360 | 12 x 30 | 875 | 350
238 | 14 x 17 | 578 | 349.7143
280 | 14 x 20 | 681 | 350.2286
350 | 14 x 25 | 851 | 350.1257
364 | 14 x 26 | 885 | 350.1099
288 | 16 x 18 | 700 | 350
320 | 16 x 20 | 778 | 350.1
400 | 16 x 25 | 972 | 349.92
416 | 16 x 26 | 1011 | 349.9615
432 | 18 x 24 | 1050 | 350
468 | 18 x 26 | 1138 | 350.1538
540 | 18 x 30 | 1313 | 350.1333
576 | 18 x 32 | 1400 | 350
480 | 20 x 24 | 1167 | 350.1
500 | 20 x 25 | 1215 | 349.92
600 | 20 x 30 | 1458 | 349.92
Square Return Air Grilles
Grille Area (sq.in) | Grille Size (in) | Airflow (cfm)
36 | 6 x 6 | 88 | 352
64 | 8 x 8 | 156 | 351
100 | 10 x 10 | 243 | 349.92
144 | 12 x 12 | 350 | 350
196 | 14 x 14 | 476 | 349.7143
256 | 16 x 16 | 622 | 349.875
324 | 18 x 18 | 788 | 350.2222
400 | 20 x 20 | 972 | 349.92
484 | 22 x 22 | 1176 | 349.8843
576 | 24 x 24 | 1400 | 350
676 | 26 x 26 | 1643 | 349.9882
900 | 30 x 30 | 2188 | 350.08
Verticle Return Air Grilles
Grille Area (sq.in) | Grille Size (in) | Airflow (cfm)
48 | 12 x 4 | 117 | 351
72 | 12 x 6 | 175 | 350
120 | 12 x 10 | 292 | 350.4
84 | 14 x 6 | 204 | 349.7143
112 | 14 x 8 | 272 | 349.7143
140 | 14 x 10 | 340 | 349.7143
96 | 16 x 6 | 233 | 349.5
128 | 16 x 8 | 311 | 349.875
192 | 16 x 12 | 467 | 350.25
180 | 18 x 10 | 438 | 350.4
216 | 18 x 12 | 525 | 350
252 | 18 x 14 | 613 | 350.2857
160 | 20 x 8 | 389 | 350.1
200 | 20 x 10 | 486 | 349.92
240 | 20 x 12 | 583 | 349.8
280 | 20 x 14 | 681 | 350.2286
320 | 20 x 16 | 778 | 350.1
360 | 20 x 18 | 875 | 350
176 | 22 x 8 | 428 | 350.1818
220 | 22 x 10 | 535 | 350.1818
96 | 24 x 4 | 233 | 349.5
144 | 24 x 6 | 350 | 350
192 | 24 x 8 | 467 | 350.25
288 | 24 x 12 | 700 | 350
336 | 24 x 14 | 817 | 350.1429
384 | 24 x 16 | 922 | 345.75
432 | 24 x 18 | 1050 | 350
364 | 26 x 14 | 885 | 350.1099
416 | 26 x 16 | 1011 | 349.9615
468 | 26 x 18 | 1138 | 350.1538
224 | 28 x 8 | 544 | 349.7143
644 | 28 x 23 | 1565 | 349.9379
180 | 30 x 6 | 438 | 350.4
240 | 30 x 8 | 583 | 349.8
300 | 30 x 10 | 729 | 349.92
360 | 30 x 12 | 875 | 350
420 | 30 x 14 | 1021 | 350.0571
480 | 30 x 16 | 1167 | 350.1
128 | 32 x 4 | 311 | 349.875
256 | 32 x 8 | 622 | 349.875
384 | 32 x 12 | 933 | 349.875
640 | 32 x 20 | 1556 | 350.1
272 | 34 x 8 | 661 | 349.9412
360 | 36 x 10 | 875 | 350
432 | 36 x 12 | 1050 | 350
504 | 36 x 14 | 1225 | 350
608 | 38 x 16 | 1478 | 350.0526
800 | 40 x 20 | 1944 | 349.92

## ASHRAE 62.1
| cfm/person | L/s·person | cfm/ft2 | L/s·m 2 | #/1000 ft2 or #/100 m2 | cfm/person | L/s·person | Air Class | Assumed Height | Outdoor ACH | Combined ACH
Correctional Facilities | [11 empty] | ASHRAE-62_1-2010.pdf
Cell | 5 | 2.5 | 0.12 | 0.6 | 25 | 10 | 4.9 | 2 | 12 | 0.625 | 1.25 | these numbers do not reconcile
Dayroom | 5 | 2.5 | 0.06 | 0.3 | 30 | 7 | 3.5 | 1 | 8 | 1.125 | 1.575
Guard stations | 5 | 2.5 | 0.06 | 0.3 | 15 | 9 | 4.5 | 1 | 8 | 0.5625 | 1.0125
Booking/waiting | 7.5 | 3.8 | 0.06 | 0.3 | 50 | 9 | 4.4 | 2 | 8 | 2.8125 | 3.375
Educational Facilities
Daycare (through age 4) | 10 | 5 | 0.18 | 0.9 | 25 | 17 | 8.6 | 2 | 8 | 1.875 | 3.1875
Daycare sickroom | 10 | 5 | 0.18 | 0.9 | 25 | 17 | 8.6 | 3 | 8 | 1.875 | 3.1875
Classrooms (ages 5–8) | 10 | 5 | 0.12 | 0.6 | 25 | 15 | 7.4 | 1 | 8 | 1.875 | 2.8125
Classrooms (age 9 plus) | 10 | 5 | 0.12 | 0.6 | 35 | 13 | 6.7 | 1 | 8 | 2.625 | 3.4125
Lecture classroom | 7.5 | 3.8 | 0.06 | 0.3 | 65 | 8 | 4.3 | 1 | 12 | 2.4375 | 2.6
Lecture hall (fixed seats) | 7.5 | 3.8 | 0.06 | 0.3 | 150 | 8 | 4 | 1 | 8 | 8.4375 | 9
Art classroom | 10 | 5 | 0.18 | 0.9 | 20 | 19 | 9.5 | 2 | 8 | 1.5 | 2.85
Science laboratories | 10 | 5 | 0.18 | 0.9 | 25 | 17 | 8.6 | 2 | 8 | 1.875 | 3.1875
University/college laboratories | 10 | 5 | 0.18 | 0.9 | 25 | 17 | 8.6 | 2 | 8 | 1.875 | 3.1875
Wood/metal shop | 10 | 5 | 0.18 | 0.9 | 20 | 19 | 9.5 | 2 | 12 | 1 | 1.9
Computer lab | 10 | 5 | 0.12 | 0.6 | 25 | 15 | 7.4 | 1 | 8 | 1.875 | 2.8125
Media center | 10 | 5 | 0.12 | 0.6 A | 25 | 15 | 7.4 | 1 | 8 | 1.875 | 2.8125
Music/theater/dance | 10 | 5 | 0.06 | 0.3 | 35 | 12 | 5.9 | 1 | 12 | 1.75 | 2.1
Multi-use assembly | 7.5 | 3.8 | 0.06 | 0.3 | 100 | 8 | 4.1 | 1 | 12 | 3.75 | 4
Food and Beverage Service | 7.5 | 3.8 | 0.18 | 0.9 | 70 | 10 | 5.1 | 2 | 12 | 2.625 | 3.5
Restaurant dining rooms
Cafeteria/fast-food dining | 7.5 | 3.8 | 0.18 | 0.9 | 100 | 9 | 4.7 | 2 | 12 | 3.75 | 4.5
Bars, cocktail lounges | 7.5 | 3.8 | 0.18 | 0.9 | 100 | 9 | 4.7 | 2 | 12 | 3.75 | 4.5
Kitchen (cooking) | 7.5 | 3.8 | 0.12 | 0.6 | 20 | 14 | 7 | 2 | 12 | 0.75 | 1.4
General | 5 | 2.5 | 0.06 | 0.3 | 25 | 10 | 5.1 | 1 | 12 | 0.625 | 1.25
Break rooms
Coffee stations | 5 | 2.5 | 0.06 | 0.3 | 20 | 11 | 5.5 | 1 | 8 | 0.75 | 1.65
Conference/meeting | 5 | 2.5 | 0.06 | 0.3 | 50 | 6 | 3.1 | 1 | 12 | 1.25 | 1.5
Corridors | – | – | 0.06 | 0.3 | – |  |  | 1 | 12 | #VALUE! | #VALUE!
Occupiable storage rooms for liquids or gels | 5 | 2.5 | 0.12 | 0.6 B | 2 | 65 | 32.5 | 2 | 8 | 0.075 | 0.975
Hotels, Motels, Resorts, Dormitories
Bedroom/living room | 5 | 2.5 | 0.06 | 0.3 | 10 | 11 | 5.5 | 1 | 8 | 0.375 | 0.825
Barracks sleeping areas | 5 | 2.5 | 0.06 | 0.3 | 20 | 8 | 4 | 1 | 8 | 0.75 | 1.2
Laundry rooms, central | 5 | 2.5 | 0.12 | 0.6 | 10 | 17 | 8.5 | 2 | 8 | 0.375 | 1.275
Laundry rooms within dwelling units | 5 | 2.5 | 0.12 | 0.6 | 10 | 17 | 8.5 | 1 | 8 | 0.375 | 1.275
Lobbies/prefunction | 7.5 | 3.8 | 0.06 | 0.3 | 30 | 10 | 4.8 | 1 | 8 | 1.6875 | 2.25
Multipurpose assembly | 5 | 2.5 | 0.06 | 0.3 | 120 | 6 | 2.8 | 1 | 12 | 3 | 3.6
Office Buildings
Breakrooms | 5 | 2.5 | 0.12 | 0.6 | 50 | 7 | 3.5 |  | 12 | 1.25 | 1.75
Main entry lobbies | 5 | 2.5 | 0.06 | 0.3 | 10 | 11 | 5.5 |  | 12 | 0.25 | 0.55
Occupiable storage rooms for dry materials | 5 | 2.5 | 0.06 | 0.3 | 2 | 35 | 17.5 |  | 8 | 0.075 | 0.525
Office space | 5 | 2.5 | 0.06 | 0.3 | 5 | 17 | 8.5 |  | 8 | 0.1875 | 0.6375
Reception areas | 5 | 2.5 | 0.06 | 0.3 | 30 | 7 | 3.5 |  | 8 | 1.125 | 1.575
Telephone/data entry | 5 | 2.5 | 0.06 | 0.3 | 60 | 6 | 3 |  | 8 | 2.25 | 2.7
Miscellaneous Spaces | 5 | 2.5 | 0.06 | 0.3 | 5 | 17 | 8.5 |  | 8 | 0.1875 | 0.6375
Bank vaults/safe deposit
Banks or bank lobbies | 7.5 | 3.8 | 0.06 | 0.3 | 15 | 12 | 6 |  | 12 | 0.5625 | 0.9
Computer (not printing) | 5 | 2.5 | 0.06 | 0.3 | 4 | 20 | 10 |  | 8 | 0.15 | 0.6
General manufacturing (excludes heavy industrial and processes using chemicals) | 10 | 5 | 0.18 | 0.9 | 7 | 36 | 18 |  | 12 | 0.35 | 1.26
Pharmacy (prep. area) | 5 | 2.5 | 0.18 | 0.9 | 10 | 23 | 11.5 |  | 12 | 0.25 | 1.15
Photo studios | 5 | 2.5 | 0.12 | 0.6 | 10 | 17 | 8.5 |  | 12 | 0.25 | 0.85
Shipping/receiving | 10 | 5 | 0.12 | 0.6 | 2 | 70 | 35 |  | 12 | 0.1 | 0.7
Sorting, packing, light assembly | 7.5 | 3.8 | 0.12 | 0.6 | 7 | 25 | 12.5 |  | 12 | 0.2625 | 0.875
Telephone closets | – | – | 0 | 0 | – |  |  |  | 8 | #VALUE! | #VALUE!
Transportation waiting | 7.5 | 3.8 | 0.06 | 0.3 | 100 | 8 | 4.1 |  | 12 | 3.75 | 4
Warehouses | 10 | 5 | 0.06 | 0.3 | – |  |  |  | 12 | #VALUE! | #VALUE!
Public Assembly Spaces
Auditorium seating area | 5 | 2.5 | 0.06 | 0.3 | 150 | 5 | 2.7 |  | 12 | 3.75 | 3.75
Places of religious worship | 5 | 2.5 | 0.06 | 0.3 | 120 | 6 | 2.8 |  | 12 | 3 | 3.6
Courtrooms | 5 | 2.5 | 0.06 | 0.3 | 70 | 6 | 2.9 |  | 12 | 1.75 | 2.1
Legislative chambers | 5 | 2.5 | 0.06 | 0.3 | 50 | 6 | 3.1 |  | 12 | 1.25 | 1.5
Libraries | 5 | 2.5 | 0.12 | 0.6 | 10 | 17 | 8.5 |  | 12 | 0.25 | 0.85
Lobbies | 5 | 2.5 | 0.06 | 0.3 | 150 | 5 | 2.7 |  | 12 | 3.75 | 3.75
Museums (children’s) | 7.5 | 3.8 | 0.12 | 0.6 | 40 | 11 | 5.3 |  | 12 | 1.5 | 2.2
Museums/galleries | 7.5 | 3.8 | 0.06 | 0.3 | 40 | 9 | 4.6 |  | 12 | 1.5 | 1.8
Residential
Dwelling unit | 5 | 2.5 | 0.06 | 0.3 | F,G | F |  |  | 8 | #VALUE! | #VALUE!
Common corridors | – | – | 0.06 | 0.3 |  |  |  |  | 8 | #VALUE! | 0
#DIV/0!
Retail | [10 empty] | #DIV/0!
Sales (except as below) | 7.5 | 3.8 | 0.12 | 0.6 | 15 | 16 | 7.8 | 2 | 12 | 0.5625 | 1.2
Mall common areas | 7.5 | 3.8 | 0.06 | 0.3 | 40 | 9 | 4.6 | 1 | 12 | 1.5 | 1.8
Barbershop | 7.5 | 3.8 | 0.06 | 0.3 | 25 | 10 | 5 | 2 | 12 | 0.9375 | 1.25
Beauty and nail salons | 20 | 10 | 0.12 | 0.6 | 25 | 25 | 12.4 |  | 12 | 2.5 | 3.125
Pet shops (animal areas) | 7.5 | 3.8 | 0.18 | 0.9 | 10 | 26 | 12.8 |  | 12 | 0.375 | 1.3
Supermarket | 7.5 | 3.8 | 0.06 | 0.3 | 8 | 15 | 7.6 |  | 12 | 0.3 | 0.6
Coin-operated laundries | 7.5 | 3.8 | 0.12 | 0.6 | 20 | 14 | 7 |  | 12 | 0.75 | 1.4
Sports and Entertainment
Sports arena (play area) | 20 | 10 | 0.18 | 0.9 | 7 | 45 | 23 |  | 12 | 0.7 | 1.575
Gym, stadium (play area) | 20 | 10 | 0.18 | 0.9 | 7 | 45 | 23 |  | 12 | 0.7 | 1.575
Spectator areas | 7.5 | 3.8 | 0.06 | 0.3 | 150 | 8 | 4 |  | 12 | 5.625 | 6
Swimming (pool & deck) | – | – | 0.48 | 2.4 | – |  |  |  | 12 | #VALUE! | #VALUE!
Disco/dance floors | 20 | 10 | 0.06 | 0.3 | 100 | 21 | 10.3 |  | 12 | 10 | 10.5
Health club/aerobics room | 20 | 10 | 0.06 | 0.3 | 40 | 22 | 10.8 |  | 12 | 4 | 4.4
Health club/weight rooms | 20 | 10 | 0.06 | 0.3 | 10 | 26 | 13 |  | 12 | 1 | 1.3
Bowling alley (seating) | 10 | 5 | 0.12 | 0.6 | 40 | 13 | 6.5 |  | 12 | 2 | 2.6
Gambling casinos | 7.5 | 3.8 | 0.18 | 0.9 | 120 | 9 | 4.6 |  | 12 | 4.5 | 5.4
Game arcades | 7.5 | 3.8 | 0.18 | 0.9 | 20 | 17 | 8.3 |  | 12 | 0.75 | 1.7
Stages, studios | 10 | 5 | 0.06 | 0.3 | 70 | 11 | 5.4 |  | 12 | 3.5 | 3.85
| cfm/person | L/s·person |  |  | Occupancy #/1000 ft2 or #/100 m2 | cfm/ft2 | L/s*m2 |  |  | ACH
Hospitals, Nursing and Convalescent Homes | [11 empty] | ASHRAE-62_1-2001.pdf
Patient rooms | 25 | 13 |  |  | 10 |  |  |  | 12 | 1.25
Medical procedure | 15 | 8 |  |  | 20 |  |  |  | 12 | 1.5
Operating rooms | 30 | 15 |  |  | 20 |  |  |  | 12 | 3
Recovery and ICU | 15 | 8 |  |  | 20 |  |  |  | 12 | 1.5
Autopsy rooms | [5 empty] | 0.5 | 2.5 |  | 12 | 2.5
Physical therapy | 15 | 8 |  |  | 20 |  |  |  | 12 | 1.5
Dry Cleaners, Laundries
Commercial laundry | 25 | 13 |  |  | 10 |  |  |  | 12 | 1.25
Commercial dry cleaner | 30 | 15 |  |  | 30 |  |  |  | 12 | 4.5
Storage, pick up | 35 | 18 |  |  | 30 |  |  |  | 12 | 5.25
Coin-operated laundries | 15 | 8 |  |  | 20 |  |  |  | 12 | 1.5
Coin-operated dry cleaner | 15 | 8 |  |  | 20 |  |  |  | 12 | 1.5
Food and Beverage Service
Dining rooms | 20 | 10 |  |  | 70 |  |  |  | 12 | 7
Cafeteria, fast food | 20 | 10 |  |  | 100 |  |  |  | 12 | 10
Bars, cocktail lounges | 30 | 15 |  |  | 100 |  |  |  | 12 | 15 |  | Supplementary smoke-removal equipment
Kitchens (cooking) | 15 | 8 |  |  | 20 |  |  |  | 12 | 1.5 |  | Makeup air for hood exhaust may require
Correctional Facilities
Cells 20 20 10 | 20 | 10 |  |  | 20 |  |  |  | 12 | 2
Dining halls 100 15 8 | 15 | 8 |  |  | 100 |  |  |  | 12 | 7.5
Guard stations 40 15 8 | 15 | 8 |  |  | 40 |  |  |  | 12 | 3
Garages, Repair, Service Stations
|  |  |  | 1.5 | 7.5 |  |  |  |  | #DIV/0!
|  |  |  | 1.5 | 7.5 |  |  |  |  | #DIV/0!

## ASHRAE 241P
Occupancy Category | STD 170 | STD 26.1 | STD 241P | Occupant | Occupant | Assumed | STD 26.1 | STD 241P | Resulting ACH | Resulting ACH
| ACH | CFM/person | CFM/person | Density | Density | Height | room | room | for STD 26.1 | for STD 241P
|  |  |  | #/1000 sqft | #/1000 sqft |  | CFM | CFM
|  |  |  | (from STD 62.1 | (from
|  |  |  | & others) | STD 62.1)
Office | np | 5 | 40 | 17 | 17 | 8 | 85 | 680 | 0.6375 | 5.1
Educational Facilities | np | 10 | 50 | 25 | 25-30 | 8 | 250 | 1250 | 1.875 | 9.375 | 9.4-11.3
Food and Beverage Facilities | np | 7.5 | 40 | 70 | 70-100 | 12 | 525 | 2800 | 2.625 | 14 | 14-20
Residential | np | 5 | 50 | 5 | no data | 8 | 25 | 250 | 0.1875 | 1.875 | 1.9
Retail | np | 7.5 | 20 | 15 | 15-40 | 12 | 112.5 | 300 | 0.5625 | 1.5 | 1.5 - 4
Gym | np | 20 | 80 | 7 | 7 | 14 | 140 | 560 | 0.6 | 2.4
Public Assembly spaces | np | 5 | 20 | 40 | 40-150 | 12 | 200 | 800 | 1 | 4 | 4 to 15
Place of religious worship | np | 5 | 30 | 120 | 120 | 40 | 600 | 3600 | 0.9 | 5.4
Healthcare exam room | 4 to 6 | 7.5 | 60 | 3 | no data | 12 | 22.5 | 180 | 0.1125 | 0.9 | 0.9
Healthcare patient room | 2 | np | 180 | 10 | 10 | 12 | #VALUE! | 1800 | #VALUE! | 9
Healthcare resident room | 2 | np | 80 | 3 | no data | 12 | #VALUE! | 240 | #VALUE! | 1.2
Common treatment area | 6 | 10 | 90 | 10 | no data | 12 | 100 | 900 | 0.5 | 4.5
Healthcare waiting room | 12 | np | 120 | 5 | no data | 12 | #VALUE! | 600 | #VALUE! | 3
Occupancy Category | STD 241P | Occupant | Occupant | Assumed | Room | Resulting ACH
| CFM/person | Density | Density | Height | CFM | for STD 241P
|  | #/1000 sqft | #/1000 sqft
|  | (for ACH | (from
|  | Calculation) | STD 62.1)
Correctional Facilities
Cell | 30 | 25 | 25 | 12 | 750 | 3.75
Dayroom | 40 | 30 | 30 | 12 | 1200 | 6
Commercial / Retail
Food and Beverage Facilities | 60 | 70 | 70-100 | 12 | 4200 | 21
Gym | 80 | 7 | 7 | 12 | 560 | 2.8
Office | 30 | 5 | 5 | 8 | 150 | 1.125
Retail | 40 | 15 | 15-40 | 12 | 600 | 3
Transportation Waiting | 60 | 100 | 100 | 30 | 6000 | 12
Educational Facilities
Classroom | 40 | 25 | 25-35 | 8 | 1000 | 7.5
Lecture Hall | 50 | 65 | 65-150 | 40 | 3250 | 4.875
Industrial
Manufacturing | 50 | 7 | 7 | 12 | 350 | 1.75
Sorting, packing, light assembly | 20 | 7 | 7 | 12 | 140 | 0.7
Warehouse | 20 | 2 | 2 | 12 | 40 | 0.2
Health Care
Exam Room | 40 | 20 | 20 | 12 | 800 | 4 |  |  |  | ASHRAE-62_1-2001.pdf
Group Treatment Area | 70 | 20 | 20 | 12 | 1400 | 7 |  |  |  | ASHRAE-62_1-2001.pdf
Patient Room | 70 | 10 | 10 | 12 | 700 | 3.5 |  |  |  | ASHRAE-62_1-2001.pdf
Resident Room | 50 | 4 | no data | 12 | 200 | 1 |  |  |  | ASHRAE-62_1-2001.pdf
Waiting Room | 90 | 10 | no data | 12 | 900 | 4.5 |  |  |  | ASHRAE-62_1-2001.pdf
Public Assembly / Sports and Entertainment
Auditorium | 50 | 150 | 150 | 40 | 7500 | 11.25
Place of Religious Worship | 50 | 120 | 120 | 40 | 6000 | 9
Museum | 60 | 40 | 40 | 12 | 2400 | 12
Convention | 60 | 40 | no data | 12 | 2400 | 12
Spectator Area | 50 | 40 | no data | 12 | 2000 | 10
Lobbies | 50 | 10 | 150 | 12 | 500 | 2.5
Residential
Common Space | 50 | 5 | no data | 8 | 250 | 1.875
Dwelling | 30 | 5 | no data | 8 | 150 | 1.125
Occupancy Category | STD 241P | Resulting | Occupant | Assumed | Room | ACH
| CFM/person | CFM/person | Density | Height | CFM | STD-101
#/1000 sqft
(for ACH
Calculation)
Correctional Facilities
Cell | 30 | 40 | 25 | 12 | 1000 | 5
Dayroom | 40 | 33.3333 | 30 | 12 | 1000 | 5
Commercial / Retail
Food and Beverage Facilities | 60 | 14.2857 | 70 | 12 | 1000 | 5
Gym | 80 | 142.8571 | 7 | 12 | 1000 | 5
Office | 30 | 133.3333 | 5 | 8 | 666.6667 | 5
Retail | 40 | 66.6667 | 15 | 12 | 1000 | 5
Transportation Waiting | 60 | 25 | 100 | 30 | 2500 | 5
Educational Facilities
Classroom | 40 | 26.6667 | 25 | 8 | 666.6667 | 5
Lecture Hall | 50 | 51.2821 | 65 | 40 | 3333.3333 | 5
Industrial
Manufacturing | 50 | 142.8571 | 7 | 12 | 1000 | 5
Sorting, packing, light assembly | 20 | 142.8571 | 7 | 12 | 1000 | 5
Warehouse | 20 | 500 | 2 | 12 | 1000 | 5
Health Care
Exam Room | 40 | 50 | 20 | 12 | 1000 | 5
Group Treatment Area | 70 | 50 | 20 | 12 | 1000 | 5
Patient Room | 70 | 100 | 10 | 12 | 1000 | 5
Resident Room | 50 | 250 | 4 | 12 | 1000 | 5
Waiting Room | 90 | 100 | 10 | 12 | 1000 | 5
Public Assembly / Sports and Entertainment
Auditorium | 50 | 22.2222 | 150 | 40 | 3333.3333 | 5
Place of Religious Worship | 50 | 27.7778 | 120 | 40 | 3333.3333 | 5
Museum | 60 | 25 | 40 | 12 | 1000 | 5
Convention | 60 | 25 | 40 | 12 | 1000 | 5
Spectator Area | 50 | 25 | 40 | 12 | 1000 | 5
Lobbies | 50 | 100 | 10 | 12 | 1000 | 5
Residential
Common Space | 50 | 133.3333 | 5 | 8 | 666.6667 | 5
Dwelling | 30 | 133.3333 | 5 | 8 | 666.6667 | 5
| ACH | CFM 1,000 Sq-Ft 8 ft Ceiling | CFM 1,000 Sq-Ft 10 ft Ceiling | CFM 1,000 Sq-Ft 12 ft Ceiling | CFM 10,000 Sq-Ft 12 ft Ceiling | CFM 10,000 Sq-Ft 24 ft Ceiling | CFM 10,000 Sq-Ft 40 ft Ceiling | CFH
| 5 | 666.6667 | 833.3333 | 1000 | 10000 | 20000 | 33333.3333 | 40000
ACH = CFM/(cu-ft*60) | 6 | 800 | 1000 | 1200 | 12000 | 24000 | 40000 | 48000
CFM = ACH*1000*8/60 | 7 | 933.3333 | 1166.6667 | 1400 | 14000 | 28000 | 46666.6667 | 56000
ACH = CFM*60/(1000*8) | 8 | 1066.6667 | 1333.3333 | 1600 | 16000 | 32000 | 53333.3333 | 64000
FFPS = CFM/(cu-ft*60) | 9 | 1200 | 1500 | 1800 | 18000 | 36000 | 60000 | 72000
| 10 | 1333.3333 | 1666.6667 | 2000 | 20000 | 40000 | 66666.6667 | 80000
| 11 | 1466.6667 | 1833.3333 | 2200 | 22000 | 44000 | 73333.3333 | 88000
| 12 | 1600 | 2000 | 2400 | 24000 | 48000 | 80000 | 96000
| 13 | 1733.3333 | 2166.6667 | 2600 | 26000 | 52000 | 86666.6667 | 104000
| 14 | 1866.6667 | 2333.3333 | 2800 | 28000 | 56000 | 93333.3333 | 112000
| 15 | 2000 | 2500 | 3000 | 30000 | 60000 | 100000 | 120000
| 60 | 8000 | 10000 | 12000 | 120000 | 240000 | 400000 | 480000
| 120 | 16000 | 20000 | 24000 | 240000 | 480000 | 800000 | 960000
| 3600 | 480000 | 600000 | 720000 | 7200000 | 14400000 | 24000000 | 28800000
| ACH | Facial Feet Per Sec 8 ft Ceiling | Facial Feet Per Sec 10 ft Ceiling | Facial Feet Per Sec 12 ft Ceiling | Facial Feet Per Sec 12 ft Ceiling | Facial Feet Per Sec 24 ft Ceiling | Facial Feet Per Sec 40 ft Ceiling | Facial Feet per Hour
| 5 | 0.0013889 | 0.0013889 | 0.0013889 | 0.0013889 | 0.0013889 | 0.0013889 | 5
Assumptions: | 6 | 0.0016667 | 0.0016667 | 0.0016667 | 0.0016667 | 0.0016667 | 0.0016667 | 6
Uniformly distributed | 7 | 0.0019444 | 0.0019444 | 0.0019444 | 0.0019444 | 0.0019444 | 0.0019444 | 7
Face is 1 cu-ft/head | 8 | 0.0022222 | 0.0022222 | 0.0022222 | 0.0022222 | 0.0022222 | 0.0022222 | 8
| 9 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 9
| 10 | 0.0027778 | 0.0027778 | 0.0027778 | 0.0027778 | 0.0027778 | 0.0027778 | 10
| 11 | 0.0030556 | 0.0030556 | 0.0030556 | 0.0030556 | 0.0030556 | 0.0030556 | 11
| 12 | 0.0033333 | 0.0033333 | 0.0033333 | 0.0033333 | 0.0033333 | 0.0033333 | 12
| 13 | 0.0036111 | 0.0036111 | 0.0036111 | 0.0036111 | 0.0036111 | 0.0036111 | 13
| 14 | 0.0038889 | 0.0038889 | 0.0038889 | 0.0038889 | 0.0038889 | 0.0038889 | 14
| 15 | 0.0041667 | 0.0041667 | 0.0041667 | 0.0041667 | 0.0041667 | 0.0041667 | 15
| 60 | 0.016667 | 0.016667 | 0.016667 | 0.016667 | 0.016667 | 0.016667 | 60
| 120 | 0.033333 | 0.033333 | 0.033333 | 0.033333 | 0.033333 | 0.033333 | 120
| 3600 | 1 | 1 | 1 | 1 | 1 | 1 | 3600
| ACH | FPM/Vent 1,000 Sq-Ft 8 ft Ceiling | FPM/Vent 1,000 Sq-Ft 10 ft Ceiling | FPM/Vent 1,000 Sq-Ft 12 ft Ceiling | FPM/Vent 10,000 Sq-Ft 12 ft Ceiling | FPM/Vent 10,000 Sq-Ft 24 ft Ceiling | FPM/Vent 10,000 Sq-Ft 40 ft Ceiling
| 5 | 166.6667 | 208.3333 | 250 | 250 | 500 | 833.3333
Assumptions: | 6 | 200 | 250 | 300 | 300 | 600 | 1000
4 vents * 1 sq-ft vent/1000 sq-ft | 7 | 233.3333 | 291.6667 | 350 | 350 | 700 | 1166.6667
| 8 | 266.6667 | 333.3333 | 400 | 400 | 800 | 1333.3333
| 9 | 300 | 375 | 450 | 450 | 900 | 1500
| 10 | 333.3333 | 416.6667 | 500 | 500 | 1000 | 1666.6667
| 11 | 366.6667 | 458.3333 | 550 | 550 | 1100 | 1833.3333
| 12 | 400 | 500 | 600 | 600 | 1200 | 2000
| 13 | 433.3333 | 541.6667 | 650 | 650 | 1300 | 2166.6667
| 14 | 466.6667 | 583.3333 | 700 | 700 | 1400 | 2333.3333
| 15 | 500 | 625 | 750 | 750 | 1500 | 2500
| 60 | 2000 | 2500 | 3000 | 3000 | 6000 | 10000
| 120 | 4000 | 5000 | 6000 | 6000 | 12000 | 20000
| 3600 | 120000 | 150000 | 180000 | 180000 | 360000 | 600000

## UV
| 3.28 | 99.9% | 99.99% | 0.185
Meters | feet | UV-C | FAR UV | Factor | ACH FAR & UV-C | Comments
| 1 | 15 |  | 0.185 | 324.3243
| 2 | 15 |  | 0.74 | 81.0811
| 3 | 15 |  | 1.665 | 36.036
| 4 | 15 |  | 2.96 | 20.2703 | Adult level
| 5 | 15 |  | 4.625 | 12.973
| 6 | 15 |  | 6.66 | 9.009
| 7 | 15 |  | 9.065 | 6.6189
2.5 | 8.2 | 15 | 12.4 | 12.4394 | 4.8234 | FAR UV claimed
| 9.2 | 15 |  | 15.6584 | 3.8318 | UV-C claimed
| 10.2 | 15 |  | 19.2474 | 3.1173
Average |  | 15 |  | 7.3245
Room Avg ACH |  | 4 |  | 8.1917
https://rzero.com/beam/
12+ eACH
99.9% in just 5 minutes
https://rzero.com/vive/
.5 M 30 sec
1.5 M 4.5 min
2.5 M 12.4 min