## Cover
Ventilation Tradeoffs
By Walter Sobkiw
2023-12-01
This analysis comes from COVID-19 Research from a Systems Perspective started in 2020.
The ventilation tradeoffs in terms of power levels is between lighting and ventilation rates.
For houses the tradeoff includes the power levels associated with appliances.

## House
| Load Actual Oct 2023 | CO2 Metric Tons / mon | Months | CO2 Metric Tons / yr | Comments
kWh Total | 354 | 0.15316 | 12 | 1.8379 | HVAC + LED lighting + appliances: refrig + dishwasher + washer + dryer + TV + Electronics
Gas CCF | 5400 | 0.297 | 12 | 3.564 | HVAC + cooking + dryer
Total |  | 0.45016 |  | 5.4019
1 CCF = 100 cuft
|  |  |  | Mech Watts / CFM 2023 | 0.5175
sqft | height | cuft | CFM | ACH peek | watt | hr/day | Duty Cycle | ACH average | kWh / mon
2300 | 10 | 23000 | 1500 | 3.913 | 776.25 | 24 | 1 | 3.913 | 558.9
2300 | 10 | 23000 | 1500 | 3.913 | 776.25 | 24 | 0.33333 | 1.3043 | 186.3
| Load Oct 2024 | CO2 Metric Tons / mon | Months | CO2 Metric Tons / yr | % using ACH avg | Comments
kWh | 168 | 0.072686 | 12 | 0.87223 | 16.14% | LED lighting + appliances: refrig + diskwasher + washer + dryer + TV + Electronics
kWh Vent | 186.3 | 0.080603 | 12 | 0.96724 | 17.9% | HVAC ventilation
kWh Tot | 354.3
Gas CCF | 5400 | 0.297 | 12 | 3.564 | 65.96% | HVAC + cooking + dryer
Total |  | 0.45029 |  | 5.4035 | 100%
ACH | kWh | kWh Vent | kWh Tot
0.33333 | 168 | 186.3 | 354.3
3.913 | 168 | 558.9 | 726.9
4 | 168 | 571.32 | 739.32
5 | 168 | 714.15 | 882.15
6 | 168 | 856.98 | 1024.98
7 | 168 | 999.81 | 1167.81
8 | 168 | 1142.64 | 1310.64
9 | 168 | 1285.47 | 1453.47
10 | 168 | 1428.3 | 1596.3
11 | 168 | 1571.13 | 1739.13
12 | 168 | 1713.96 | 1881.96
1. Electricity: 11,880 kWh per home × 884.2 lbs CO2 per megawatt-hour generated × (1/(1-0.073)) MWh generated/MWh delivered × 1 MWh/1,000 kWh × 1 metric ton/2,204.6 lb = 5.139 metric tons CO2/home.
2. Natural gas: 41,590 cubic feet per home × 0.0550 kg CO2/cubic foot × 1/1,000 kg/metric ton = 2.29 metric tons CO2/home
3. Propane: 42 gallons per home × 1/42 barrels/gallon × 235.0 kg CO2/barrel × 1/1,000 kg/metric ton = 0.23 metric tons CO2/home
4. Fuel oil: 27 gallons per home × 1/42 barrels/gallon × 426.1 kg CO2/barrel × 1/1,000 kg/metric ton = 0.27 metric tons CO2/home
Total CO2 emissions for energy use per home: 5.139 metric tons CO2 for electricity + 2.29 metric tons CO2 for natural gas + 0.23 metric tons CO2 for propane + 0.27 metric tons CO2 for fuel oil = 7.93 metric tons CO2 per home per year.
https://www.epa.gov/energy/greenhouse-gases-equivalencies-calculator-calculations-and-references
https://www.epa.gov/avert/download-avert
https://www.epa.gov/avert/avert-web-edition

## Rooms
4.4
Room | sqft | sq-m | Lux | LM | LM/sqft | LED LM/Watt | # of 850 LM Bulbs | LED Watts Tot | LED Watts / Bulb | incandescent Watts Tot | Comments
Classroom A | 1000 | 92.9506 | 300 | 27885.1874 | 27.8852 | 63 | 32.8061 | 442.622 | 13.4921 | 1947.5369 | tutoring sessions, practical exercises and physical exercise
Classroom B | 1000 | 92.9506 | 500 | 46475.3123 | 46.4753 | 63 | 54.6768 | 737.7034 | 13.4921 | 3245.8948 | reading rooms, prep rooms and workshops
Classroom C | 1000 | 92.9506 | 750 | 69712.9685 | 69.713 | 63 | 82.0153 | 1106.5551 | 13.4921 | 4868.8422 | Art and technical drawing classrooms
Garage | 400 | 37.1802 | 100 | 3718.025 | 9.2951 | 63 | 4.3741 | 59.0163 | 13.4921 | 259.6716
Bathroom | 36 | 3.3462 | 500 | 1673.1112 | 46.4753 | 63 | 1.9684 | 26.5573 | 13.4921 | 116.8522
| Ceiling | 12
Room | sqft | cuft | ACH | CFM | Watts / CFM | Watts Tot |  |  |  | CFM = ACH*cuft/60
Classroom | 900 | 10800 | 1 | 180 | 0.5175 | 93.15 |  |  |  | https://blog.secom.es/en/adequately-lit-classrooms/
Classroom | 900 | 10800 | 2 | 360 | 0.5175 | 186.3 |  |  |  | 1 meter = 3.28084 ft
Classroom | 900 | 10800 | 3 | 540 | 0.5175 | 279.45 |  |  |  | lux = LM/sq-meter
Classroom | 900 | 10800 | 4 | 720 | 0.5175 | 372.6 |  |  |  | LM = lux * sq-meter
Classroom | 900 | 10800 | 5 | 900 | 0.5175 | 465.75
Classroom | 900 | 10800 | 6 | 1080 | 0.5175 | 558.9 |  |  |  | 300 lux for young people and 500 lux for adult education and evening classes.
Classroom | 900 | 10800 | 7 | 1260 | 0.5175 | 652.05 |  |  |  | sitting room or bedroom 10-20 lumens per square foot
Classroom | 900 | 10800 | 8 | 1440 | 0.5175 | 745.2 |  |  |  | bathroom or kitchen 70-80 lumens per square foot
Classroom | 900 | 10800 | 9 | 1620 | 0.5175 | 838.35 |  |  |  | incandescent bulbs 14.3 lumens/watt
Classroom | 900 | 10800 | 10 | 1800 | 0.5175 | 931.5 |  |  |  | incandescent bulbs 15 lumens/watt
Classroom | 900 | 10800 | 11 | 1980 | 0.5175 | 1024.65 |  |  |  | LED bulbs 75-110 lumens/watt
Classroom | 900 | 10800 | 12 | 2160 | 0.5175 | 1117.8 |  |  |  | LED bulbs 63 lumens/watt
Room | sqft | cuft | eACH |  | UV Watts / cuft | Watts Tot |  |  |  | https://blog.secom.es/en/adequately-lit-classrooms/
Classroom | 900 | 10800 | 12 |  | 0.017276 | 186.5854 |  |  |  | https://www.voltlighting.com/learn/lumens-to-watts-conversion-led-bulb
Classroom | 1000 | 12000 | 12 |  | 0.017276 | 207.3171 |  |  |  | https://www.pooky.com/blogs/inspiration/how-much-light-do-you-need-in-a-room
https://www.eaton.com/tw/en-us/company/news-insights/lighting-resource/trends/led-trends-more-lumens-per-watt.html
https://www.any-lamp.com/blog/lumen-and-lux
| Ceiling | 12
Room | sqft | cuft | ACH | CFM | CFH | Watts / CFM | Watts Tot (1000 sqft) | Watts Tot (1 cuft)
Classroom | 1000 | 12000 | 1 | 200 | 12000 | 0.5175 | 103.5 | 0.008625
Classroom | 1000 | 12000 | 2 | 400 | 24000 | 0.5175 | 207 | 0.01725
Classroom | 1000 | 12000 | 3 | 600 | 36000 | 0.5175 | 310.5 | 0.025875
Classroom | 1000 | 12000 | 4 | 800 | 48000 | 0.5175 | 414 | 0.0345
Classroom | 1000 | 12000 | 5 | 1000 | 60000 | 0.5175 | 517.5 | 0.043125
Classroom | 1000 | 12000 | 6 | 1200 | 72000 | 0.5175 | 621 | 0.05175
Classroom | 1000 | 12000 | 7 | 1400 | 84000 | 0.5175 | 724.5 | 0.060375
Classroom | 1000 | 12000 | 8 | 1600 | 96000 | 0.5175 | 828 | 0.069
Classroom | 1000 | 12000 | 9 | 1800 | 108000 | 0.5175 | 931.5 | 0.077625
Classroom | 1000 | 12000 | 10 | 2000 | 120000 | 0.5175 | 1035 | 0.08625
Classroom | 1000 | 12000 | 11 | 2200 | 132000 | 0.5175 | 1138.5 | 0.094875
Classroom | 1000 | 12000 | 12 | 2400 | 144000 | 0.5175 | 1242 | 0.1035
| Ceiling | 12
Room | sqft | cuft | ACH | CFM | CFH | Watts / CFM | Watts Tot
Classroom | 0.083333 | 1 | 1 | 0.016667 | 1 | 0.5175 | 0.008625
Classroom | 0.083333 | 1 | 2 | 0.033333 | 2 | 0.5175 | 0.01725
Classroom | 0.083333 | 1 | 3 | 0.05 | 3 | 0.5175 | 0.025875
Classroom | 0.083333 | 1 | 4 | 0.066667 | 4 | 0.5175 | 0.0345
Classroom | 0.083333 | 1 | 5 | 0.083333 | 5 | 0.5175 | 0.043125
Classroom | 0.083333 | 1 | 6 | 0.1 | 6 | 0.5175 | 0.05175
Classroom | 0.083333 | 1 | 7 | 0.11667 | 7 | 0.5175 | 0.060375
Classroom | 0.083333 | 1 | 8 | 0.13333 | 8 | 0.5175 | 0.069
Classroom | 0.083333 | 1 | 9 | 0.15 | 9 | 0.5175 | 0.077625
Classroom | 0.083333 | 1 | 10 | 0.16667 | 10 | 0.5175 | 0.08625
Classroom | 0.083333 | 1 | 11 | 0.18333 | 11 | 0.5175 | 0.094875
Classroom | 0.083333 | 1 | 12 | 0.2 | 12 | 0.5175 | 0.1035

## Lighting
Activity | Illuminance |  | LM/Watt
| (lx, lumen/m2) | incandescent | 14.3
Public areas with dark surroundings | 20 - 50 | LED | 63
Simple orientation for short visits | 50 - 100 | Ratio | 4.4056
Areas with traffic and corridors - stairways, escalators and travelators - lifts - storage spaces | 100 | https://www.eaton.com/tw/en-us/company/news-insights/lighting-resource/trends/led-trends-more-lumens-per-watt.html
Working areas where visual tasks are only occasionally performed | 100 - 150
Warehouses, homes, theaters, archives, loading bays | 150
Coffee break room, technical facilities, ball-mill areas, pulp plants, waiting rooms, | 200
Easy office work | 250
Class rooms | 300
Normal office work, PC work, study library, groceries, show rooms, laboratories, check-out areas, kitchens, auditoriums | 500
Supermarkets, mechanical workshops, office landscapes | 750
Normal drawing work, detailed mechanical workshops, operation theaters | 1000
Detailed drawing work, very detailed mechanical works, electronic workshops, testing and adjustments | 1500 - 2000
Performance of visual tasks of low contrast and very small size for prolonged periods of time | 2000 - 5000
Performance of very prolonged and exacting visual tasks | 5000 - 10000
Performance of very special visual tasks of extremely low contrast and small size | 10000 - 20000
https://www.lumistrips.com/lumistrips-en-lumen-lux-calculator

## QII Costs
Assumptions | sq-ft
Room Size | 1000
Facility Size | 1000
Measurement Spaces | 1
Cost Estimate Items | Event | Min | Spaces | Duty Cycle | Cost Hrs / yr | Benefit Hrs / yr | Comments
Room Observations Checklists | Bi-annual | 1 | 1 | 2 | 0.033333 |  | Performed by independent Ventilation POC and or Health and Safety
Facility Observations Checklist | Bi-annual | 1 | 1 | 2 | 0.033333 |  | Performed by independent Ventilation POC and or Health and Safety
Ventilation Public Disclosure | quarterly | 30 | 1 | 4 | 2 |  | Performed by independent Ventilation POC and or Health and Safety
ACH Level Measurement | annual | 5 | 1 | 1 | 0.083333 |  | Can become 0 with new proposed in room ACH level panel
Room Observations Daily Record (ODC) | daily | 1 | 1 | 260 |  | 0.21667 | Performed by room hosts 52*5*.1 (5% by dedicated staff)
Room Observations Checklists (ODC) | weekly | 1 | 1 | 52 |  | 0.86667 | Performed by room hosts, IT, student volunteers, and or Janitorial Staff
ACH Level Measurement (ODC) | weekly | 1 | 1 | 52 |  | 0.86667 | Performed by room hosts, IT, student volunteers, and or Janitorial Staff
Occupant Observations (ODC) | real time | 1 | 1 | 13 |  | 0.21667 | Performed by room occupants 52*5*.05
QII Reports | weekly | 1 | 1 | 52 | 0.86667 |  | Performed by independent Ventilation POC and or Health and Safety
ODC Reports | weekly | 1 | 1 | 52 |  | 0.86667 | Performed by independent Ventilation POC and or Health and Safety
Annual Total Hours |  |  |  |  | 3.0167 | 3.0333
|  | Hours | $100/hr | Capital Equip (anemometers)
Annual Cost QII |  | 3.0167 | 301.6667 | 20
Annual Benefit ODC |  | 3.0333 | 303.3333 | 20

## Roof Solar
Number of Floors in Building | Electricity Produced By Roof Solar Installation
1 | 100%
2 | 50%
3 | 33.33%
4 | 25%
5 | 20%
6 | 16.67%
7 | 14.29%
8 | 12.5%
9 | 11.11%
10 | 10%